## Slide 1
Sebastian Dänner Product Manager HIQuad X
HIQuad X Technical Product Presentation

## Slide 2
HIMA Smart Safety Platform
Notes: Moving on to our products.
As you are about to see, no matter what the requirements a safety system has, we create the perfect solution.
What’s more, our systems are always reliable, cost effective, and smart.
All our systems are based on open communication protocols, making them easy to integrate with any control system or automation environment.

## Slide 3
The Four Customer Perspectives
Rely on decades of safety experience, proven technologies, and expert services.
Run your plant safely, but efficiently and profitably at the same time.
Reliability
Profitability
Always comply with safety standards.
Your safety automation and critical assets are always protected.
Safety
Security
Notes: The four key outcomes of the Smart Safety concept are safety, security, reliability, and profitability.
Safety: Fulfill the requirements of safety standards and regulations, and reduce risks.
Security: Protect your automation systems and critical assets from cyberattacks and other cyber risks.
Reliability: Expert services and proven technologies keep your plants and machinery up and running.
Profitability: Increase the efficiency and yield of your plant, while keeping it safe at the same time.

## Slide 4
The world’s first scalable safety platform with built-in cybersecurity.
Your benefit: Reduce the complexity of your safety systems and stay protected against ever-increasing risks.
Smart Safety Platform
Notes: First of all, allow me to explain our brand-new Smart Safety Platform. It is the world‘s first complete, cybersecure safety platform. It comprises 4 HIMA products (HIMax, HIMatrix, HIQuad X, and HIJunctionBox). These share the same engineering tool, the same security concept, the same firmware, and the same communication protocol.

## Slide 5
HIMA Product Portfolio – The Mission
Support existing installations with a long term strategy for investment protection.
Smart Safety Platform including HIQuad X.
Continuous developments strengthens our Smart Safety Platform.
Safe interoperability of HIMA Systems including HIQuad and optimization of their integration.
Comprehensive modernization services for Legacy Systems.
Future aim: Expanding our HIMA safety product portfolio.
Notes: Here you can see all of our safety control systems.
They can be used up to SIL 3 and, in the rail industry, up to SIL 4 according to CENELEC standards. Our hardwired safety controller Planar4 is even approved for use up to SIL 4, the highest safety level there is.

## Slide 6
2000
1000
500
200
100
Performance
I/O Points
Product Portfolio HIMA safety PLCs – 2020

## Slide 7
Product Launch HIQuad X
The flexible, scalable safety control system for a wide range of applications.
Notes: HIQuad systems are highly reliable and can be configured flexibly. They are designed for small and midsized applications in the process industry.
They protect both central and distributed applications with maximum fault tolerance.
They are so flexible that they even allow you to make program changes during operation.
Since launch, HIQuad has become the benchmark for reliable and cost-effective safety solutions in the process industry.

## Slide 8
Why the name HIQuad X?
HIQuad stands for reliability - 1,000 times proven.
The capital letter X – for SILworX programming.
We want…
to fulfil our long term lifecycle commitments.
to protect our installed base of more than 10.000 HIQuad systems.
to be a trustful partner for safety technology.
We offer our customers …
an attractive way into the SILworX world.
to keep the majority of his investments.
to continue his proven in use safety technology and to improve it selectively.
Why are we developing HIQuad X?
Notes: Warum kam es zu dem Name HIQuad X?
HIQuad ist DAS Basis Sicherheitssystem der HIMA. In vielen Ländern (China, Malaysia, aber auch in Europa) repräsentiert HIQuad und Ihre Eigenschaften die HIMA. Sie ist prägend und hat einen ausgesprochen angesehenen Name. Er steht für Zuverlässigkeit. HIQuad ist eine Marke mit einem Wert. Diesen Wert wollen wir erhalten und in die Zukunft überführen.
Das X steht für die etablierte HIMA Plattform, die wir mit SILworX bedienen. Seit HIMax ist das X mit der Performance unserer Sicherheitssteuerungen gleichzusetzen. Es ziert jedes HIMax Modul. Auch die Verfügbarkeit wird seit HIMax mit X-MR Architektur auf ein neues Level gehoben.
X bedeutet:
Verfügbarkeit
Nonstop Operation
Flexibilität
State of the art Safety & Security
Die HIQuad mit dem Mehr an Emotionen des X auszustatten, war seit Beginn der Idee das Ziel.

## Slide 9
HIQuad X consisting of H51X/H41X is going to be the future Basic-Safety System
Applicable for up to SIL 3
With standard and high availability and integrated intrinsically safety modules HIQuad X (H51X/H41X) will be the future of HIQuad (H41q/H51q).
HIQuad X (H41X) is going to serve small systems with affordable costs.
Product Positioning within HIMA Product-Portfolio

## Slide 10
New installations and modernization of existing systems:
Up to date security concept
One engineering platform
Increased performance
Enhanced reload functionalities
Comprehensive communication options
Safe communication among HIMA systems
Modernization of existing HIQuad systems:
No change of HIQuad I/O including field wiring
Shorter plant shutdown times for upgrades
Less effort upgrades compared to new installations
What are the benefits of HIQuad X?
H51X
H41X
New
New

## Slide 11
HIQuad X – System Features
The flexible, scalable safety control system for a wide range of applications.
Notes: HIQuad systems are highly reliable and can be configured flexibly. They are designed for small and midsized applications in the process industry.
They protect both central and distributed applications with maximum fault tolerance.
They are so flexible that they even allow you to make program changes during operation.
Since launch, HIQuad has become the benchmark for reliable and cost-effective safety solutions in the process industry.

## Slide 12
Design:
Modernized Design
Local diagnosis concept improved
Improved haptics
F-CPU 01: Processor module H51X, H41X (2 x RJ-45, SIL 3)
F-COM 01: Communication module for Ethernet, Profibus DP and serial communication(2 x RJ-45, 1x 9-pole D-Sub (2x RS 485)
F-IOP 01: I/O processing module (SIL 3) with redundant system bus
F-PWR 01: Power supply module 24 VDC / 5 VDC, 50 W, H41X, H51X
F-PWR 02: Watchdog supply module for extension rack, H51X
Design of new modules

## Slide 13
HIQuad X – New performance dimension
Chart: 
| 0 | 200 | 400 | 600 | 800 | 1000 | 2000
cycle time [ms] | 20 | 48 | 76 | 104 | 132 | 160
Higher performance through
  Better REAL calculation possibilities
  Lower system cycle times and reaction times
  E.g. 200 I/O points at 50 ms cycle time possible
New application opportunities
  Formerly separated HIQuad systems can be combined – Multitasking helps for separation needs
Allows optimization of application program, which improves
  Better understanding of application
  Shorter maintenance time through faster failure tracking
  Higher safety awareness through clearer structure
A target cycle time can be used for HIQuad X in SILworX
e.g. to emulate a similar behaviour of the former HIQuad system

## Slide 14
HIQuad X – flexible system architecture
Redundancy options at every point
CPU modules
I/O modules
I/O Racks
COM modules
Cross connection increases system availability
Every I/O module is connected to every CPU
CPU modules share the results among each other
Power Supply
Power Supply
SIL3
Input
Output
In
CPU
Out
In
Out
& maximum available
CPU
No degradation of safety and
availability

## Slide 15
New: Ethernet based system bus communication between Basic Rack and I/O Extension Racks
  Fault tolerant bus concept with two F-CPU 01
  Increased system bus fault tolerance on H51X
  Physical separation with Ethernet infrastructure between F-CPU 01 and F-IOP 01
  Higher system robustness through usage of Ethernet system bus (no cross talking over the lines)
  F-IOP 01 provides freedom of interference from I/O to F-CPU 01
Reload technology of Smart Safety Platform
  Reload with one F-CPU 01
  Add, change, delete
    Application
    Hardware
    communication
HIQuad X – Availability

## Slide 16
HIQuad X – How a Reload works
t
AP 1
AP 2
AP 1
AP 2
AP 1
AP 2
AP 1
AP 2
DOWNLOAD means to change the application the PES needs to be STOPPED
RELOAD means the change of the application program is done ONLINE

## Slide 17
Operation of application in A
Reload of changed application in B
Verification of changes
RELOAD: Online Changes & Modifications
Memory A
Memory B

## Slide 18
Memory A
Memory B
RELOAD: Online Changes & Modifications
Operation of Application in A
Memory B
Verification of changes
Operation of application in B
Reload of changed application in B
Switch over to B in the next cycle
Operation of application in A
Memory A
Memory A
Memory B

## Slide 19
HIQuad X – Engineering
One common engineering Tool SILworX
Less space compared to former HIQuad architectures
Flexible I/O configuration
Wiring effort reduced – higher degree of integration
  New backplane of F-BASE RACK 01 & 02 reduces susceptibility (less wiring and open contacts)
  M 4410: Cover plate for the rear side of the F-BASE RACKs (to protect open contacts)
Accelerated Start-Up through enhanced diagnosis
Basic Rack only 4 units high
Later: New fan with vacuum evacuation F-FAN 01

## Slide 20
Automatic restart after removed module failure and field error
Automatic start-up of configured modules
Higher degree of diagnosis with SILworX (extended diagnostic memory)
Improved I/O diagnosis on F-IOP 01
  Signalling of faulty module
  Signalling of faulty channel for intelligent modules
Integrated power supplies
  Power supplies with self diagnosis
  Feedback of condition to F-CPU 01 and SILworX
  Power supplies need no manual voltage matching
Improved maintenance in running operation due to
  modular structure of system improves handling
  Better exchangeability of system components
HIQuad X – Maintenance Support

## Slide 21
HIQuad X – H51X
The flexible, scalable safety control system for a wide range of applications.
Notes: HIQuad systems are highly reliable and can be configured flexibly. They are designed for small and midsized applications in the process industry.
They protect both central and distributed applications with maximum fault tolerance.
They are so flexible that they even allow you to make program changes during operation.
Since launch, HIQuad has become the benchmark for reliable and cost-effective safety solutions in the process industry.

## Slide 22
Better REAL-calculations
  Processing of I/O modules on F-IOP 01 increases performance
Up to 16 I/O racks
With up to 256 I/O modules
And up to 4096 I/O points
System bus length between two racks up to Ethernet limits (~50 m)
H51X – Capability Characteristics

## Slide 23
H51X – SIL3 architecture mono
F-BASE RACK 01
I/O #1
I/O #2
I/O #3
I/O #4
I/O #5
I/O #6
I/O #8
I/O #7
I/O #9
I/O #10
I/O #11
I/O #12
I/O #13
I/O #14
I/O #15
I/O #16
F-IOP 01
F 7133
F 7133
F 7133
F 7133
I/O #1
I/O #2
I/O #3
I/O #4
I/O #5
I/O #6
I/O #8
I/O #7
I/O #9
I/O #10
I/O #11
I/O #12
I/O #13
I/O #14
I/O #15
I/O #16
F-IOP 01
F 7133
F 7133
F 7133
F 7133
System Configuration
max. 16 I/O extension racks
In 1 or 2 lines
Advantage: Fault tolerance up to 2 I/O extension racks
F-PWR 01
F-PWR 01
F-PWR 01
F-PWR 01
F-PWR 01
F-PWR 02
F-PWR 02
F-CPU 01
F-COM 01
blank
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01

## Slide 24
blank
F-BASE RACK 01
blank
F-CPU 01
I/O #1
I/O #2
I/O #3
I/O #4
I/O #5
I/O #6
I/O #8
I/O #7
I/O #9
I/O #10
I/O #11
I/O #12
I/O #13
I/O #14
I/O #15
I/O #16
F-IOP 01
F 7133
F 7133
F 7133
F 7133
I/O #16
I/O #1
I/O #2
I/O #3
I/O #4
I/O #5
I/O #6
I/O #8
I/O #7
I/O #9
I/O #10
I/O #11
I/O #12
I/O #13
I/O #14
I/O #15
F-IOP 01
F 7133
F 7133
F 7133
F 7133
H51X – SIL3 architecture redundant
F-PWR 01
F-PWR 01
F-PWR 01
F-PWR 01
F-PWR 01
F-PWR 02
F-PWR 02
F-CPU 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
F-COM 01
System Configuration:
max. 16 I/O extension racks
2 ring structures
Advantage: Fault tolerance
E.g. exchange of I/O extension racks without loosing connection to other I/O extension racks.

## Slide 25
The flexible, scalable safety control system for a wide range of applications.
HIQuad X – H41X
Notes: HIQuad systems are highly reliable and can be configured flexibly. They are designed for small and midsized applications in the process industry.
They protect both central and distributed applications with maximum fault tolerance.
They are so flexible that they even allow you to make program changes during operation.
Since launch, HIQuad has become the benchmark for reliable and cost-effective safety solutions in the process industry.

## Slide 26
Common usage of H51X components
Up to 12 I/O modules in one rack
Up to 28 I/O modules in two racks
Up to 224 I/O points
For redundant I/O modules additional I/O rack can be used. Electrical and communication connections are foreseen
Engineering recommendation: Instead of using H41X with I/O rack, please use H51X
HIQuad X – H41X system
2x F-PWR 01
2x F-CPU
2x F-COM
1x F-IOP
12x I/O

## Slide 27
F-BASE RACK 02
I/O #1
I/O #2
I/O #3
I/O #4
I/O #5
I/O #6
I/O #8
I/O #7
I/O #9
I/O #10
I/O #11
I/O #12
F-IOP 01
F-COM 01
F-COM 01
F-PWR 01
F-PWR 01
F-CPU 01
blank
H41X – Architecture Mono

## Slide 28
blank
F-CPU 01
F-CPU 01
F-COM 01
F-COM 01
H41X – Architecture Redundant
I/O #1
I/O #2
I/O #3
I/O #4
I/O #5
I/O #6
I/O #8
I/O #7
I/O #9
I/O #10
I/O #11
I/O #12
I/O #13
I/O #14
I/O #15
I/O #16
F-IOP 01
F 7133
F 7133
F 7133
F 7133
I/O #1
I/O #2
I/O #3
I/O #4
I/O #5
I/O #6
I/O #8
I/O #7
I/O #9
I/O #10
I/O #11
I/O #12
F-IOP 01
F-PWR 01
F-PWR 01

## Slide 29
HIQuad X Hardware Overview

## Slide 30
Ersatzteile / spare parts |  |  | 
HIQuad X | TN / Part No. | Deutsch | Englisch
F-CPU 01 | 98 4866102 | Prozessormodul H51X, H41X (2x RJ-45, SIL 3), Schutzlackierung | Processor module H51X, H41X (2x RJ-45, SIL 3), coated
F-COM 01 | 98 4867202 | Kommunikationsmodul für Ethernet, Profibus DP und serielle Kommunikation (2x RJ-45, 1 x 9-polige D-SUB (2x RS 485), Schutzlackierung | Communication module for Ethernet, Profibus DP and serial communication (2x RJ-45, 1 x 9-pole D-Sub 2x RS 485)
F-BASE RACK 01 | 99 6142100 | Basisrack H51X, 19 Zoll, 4 HE | Base rack H51X, 19 inches, 4 units high
F-BASE RACK 02 | 99 6142200 | Basisrack H41X, 19 Zoll, 4 HE, 12 E/A Steckplätze | Base rack H41X, 19 inches, 4 units high, 12 slots for I/O modules
F-BASE RACK 11 | 99 6140600 | Bleibt bestehen K 1406 Erweiterungsrack H41X, H51X, H51q, 19 Zoll, 4 HE, 16 E/A Steckplätze | Remains the same K 1406 Extention rack H41X/H51X, H51q, 19 inches, 4 units high, 16 slots for I/O modules
(=K 1406) |  |  | 
F-PWR 01 | 98 4714102 | Netzgerätemodul 24 VDC / 5 VDC, 50W, H41X, H51X, Schutzlackierung | Power supply module 24 VDC / 5 VDC, 50 W, H41X, H51X
F-PWR 02 | 98 4714202 | Watchdog Versorgungsmodul für Erweiterungsracks, H51X, Schutzlackierung | Watchdog supply module for extension rack, H51X
F-IOP 01 | 98 4850102 | 2 E/A Verarbeitungsmodul (SIL 3) mit redundantem Systembus, Schutzlackierung | I/O processing module (SIL 3) with redundant system bus
HIQuad X – Ersatzteile / Spare Parts

## Slide 31
I/O modules | SIL | Channels | OC/SC | Ex | Note
Input modules digital |  |  |  |  | 
F 3221 |  | 16 | - | - | Contacts, 1 signal 24 VDC
F 3224A |  | 4 | - | yes | Contacts, 1 signal, SN-, proximity switches, wired contacts, ATEX
F 3236 | 3 | 16 | - | - | Contacts, 1 signal 24 VDC
F 3240 | 3 | 16 | - | - | Contacts, 1 signal 110 VDC/127 VAC
F 3248 | 3 | 16 | - | - | Contacts, 1 signal 48 VDC
Input modules Initiator |  |  |  |  | 
F 3237 | 3 | 8 | yes | - | SN-, proximity switches, wired contacts
F 3238 | 3 | 8 | yes | yes | SN-, proximity switches, wired contacts, 8 DU wide, ATEX
Input modules analog |  |  |  |  | 
F 6215 | 3 | 8 | yes | - | Current, voltage, Pt100
F 6217 | 3 | 8 | yes | - | Current, voltage
F 6220* | 3 | 8 | yes | - | Thermoelemente, Pt100, ATEX, *supported in HIQuad X, but EOL reached!
F 6221 | 3 | 8 | yes | yes | Current, voltage, ATEX
Special modules |  |  |  |  | 
F 5220 | 3 | 2 | yes | - | Counter module initiator, 5 VDC, 24 V DC to 1 MHz, 2 integral digital outputs 24 VDC to 0.5 A
Supported I/O modules – Input
Notes: * Module supported in HIQuad X, but it is since 2019 obsolete.

## Slide 32
I/O modules | SIL | Channels | OC/SC | Ex | Note
Output modules digital |  |  |  |  | 
F 3322 |  | 16 | - | - | 24 VDC to 0.5 A
F 3325 | 3 | 6 | - | yes | Ex transmitter supply module for F 6221, ATEX
F 3330 | 3 | 8 | - | - | 24 VDC to 0.5 A
F 3331 | 3 | 8 | yes | - | 24 VDC to 0.5 A
F 3333 | 3 | 4 | - | - | 24 VDC to 2 A
F 3334 | 3 | 4 | yes | - | 24 VDC to 2 A
F 3335 | 3 | 4 | - | yes | 24 VDC, ATEX
F 3349* | 3 | 8 | yes | - | 24 VDC/48 V DC to 0.5 A
F 3422 |  | 8 | - | - | Relay module, 30 VAC/DC, 120 W, floating NO contact
F 3430 | 3 | 4 | - | - | Relay module, 110 VDC/250 V AC to 4 A
Output modules analog |  |  |  |  | 
F 6705 | 3 | 2 | - | - | Current
F 6706 |  | 2 | - | - | Current
Supported I/O modules – Output
Notes: *F 3349 is supported in HIQuad X, but
Hardware revision AS00 is recommended to be exchanged with hardware revision AS01
With hardware revision AS01 the availability is increased.
The hardware revision is written on the label
The new color code RAL9002 (white) is a strong indicator that you have the up to date hardware revision AS01
The old color code RAL7032 (industry-grey) is a strong indicator that you have the hardware revision AS00, which is recommended to be exchange during the modernization from HIQuad to HIQuad X

## Slide 33
HIQuad X – Communication

## Slide 34
Benefit:
Partial system modernization possible
Enables partial plant modernization in incremental steps
Freedom of system choice – allows the combination of all HIMA PES
Enables the simple expansion of applications and plants
One Safe Communication Platform HIQuad X – HIMax – HIMatrix – HIQuad

## Slide 35
  Data transmission at 1 GBit/s
  Fast response times, even for networked applications
  Utilizes standard Ethernet components and functions for safety-critical applications
  Use of any transmission media
  255 safeethernet connections per System (between PES red. Connection possible)
  Intelligent, diverse redundancy concepts
  Unique: reloadable safety protocol
Safety-Related Networking via safeethernet
safeethernet on any Ethernet infrastructure (black channel) Virtually no limit in the extension

## Slide 36
HK- COM3
HK- COM3
≤ 64 Connections
≤ 505 Bytes
HIBUS
V1 and/or V2
192.168.0.X
Safe communication – HIPRO-S V2
XML-Export
HIPRO-S V2 configuration
V5.6
≥ V8.4

## Slide 37
HIQuad X – Communication
Hardware-Features:
H51X: Peer-to-peer connection from every F-CPU 01 to every of 10x F-COM 01
H41X: Peer-to-peer connection from every F-CPU 01 to every of 2x F-COM 01
2 ETH interfaces per F-CPU 01 for PADT and safeethernet communication
2 ETH interfaces per F-COM 01 for all communication protocols
Serial interface for existing old protocols
Parameterization and configuration:
Complete IP address range can be used
Subnet mask settings can be changed
V-LAN settings for network segmentation can be parameterized
Supports standard and safety protocols

## Slide 38
HIQuad X – Communication Protocols
Safety Communication:
safeethernet
HIPRO-S V2
Standard Communication:
Modbus TCP Master & Slave
Modbus RTU Master & Slave
Profibus DP Slave
X-OPC Server for OPC DA and OPC A&E
COM User Task (CUT) individual protocol programming

## Slide 39
HIMA Systems Integrate with All Leading DCSs
Notes: Distributed control systems (DCSs) are crucial for controlling and monitoring your plants. HIMA safety systems can be integrated into your existing distributed control systems, but still run independently and are physically separated. This makes an important contribution to plant safety, enables central monitoring of all components, and prevents errors in the distributed control system from affecting the safety system. It continues running smoothly.
Customers can combine the best distributed control system for their application and the most suitable safety solution. This is only possible with HIMA, as HIMA is the only company with the necessary expertise. DCS integration is an extremely complex area, especially as there are so many vendors. At HIMA, we have established our own Competence Center, 100% dedicated to this task.

## Slide 40
HIQuad X – Security
Notes: Änderungswunsch:
Darstellung einheitlich machen.
Aus den 3 Folien möglichst 2 Folien machen. Gleichartige Darstellung für Tunneln und external extraction.

## Slide 41
Security – Protective Measurements
PC Environment
Antivirus
Firewall
Engineering Tool
SILworX
CRC protection
User Management
Communication
Physical separation
Open Standards
Smart Safety Platform
HIMax / HIQuad X / HIMatrix
Safety Application
Access protection
Port Locking
CRC protection
Change control
Access protection
Change Management
Only configured Data
Key Switch

## Slide 42
Cyber Security – layer of protection via virtual and physical segregation
Systembus
  Virtual segregation via firewall on safety CPU
  Allow configured data exchange only
  Use valid telegrams only
  SIL3 Memory protection: Usage of independent memory
  SIL3 timing protection: Uses only configured COM time slice
  Physical segregation via separate COM Module
  Firewall features as above
  Additional independent layer of protection
Standard communication
safety
com

## Slide 43
Prepare HIQuad X Modernization

## Slide 44
ELOP II Modernization Service
≥V8.xx.x
≥V5.6
Logic Conversion
Modernization Service by HIMA
ELOP II

## Slide 45
HIQuad X – Modernization effort
Less effort compared to a completely new installation!
Acceptance test needs to be renewed
Logic conversion needs to be reworked
Not all I/O modules are reusable, only modules of price list 2016
For installation
  Central rack needs to be renewed
  New module F-IOP 01 allows system bus
X-OPC Server and SNTP are the substitutes
Notes: Change:
No Display – SILworX must be used for
  CRC indication of system
  Operating system revision

## Slide 46
Organisation
    Installed base
    When should the shutdown be implemented?
Inventory of HIQuad systems
  Of which modules consists the system including hardware revision?
HIQuad network plan
  How many systems run in one network (networking partners and addresses)?
  Modbus Master IP-address and Modbus address list
  Which safe communication runs within the system (HIPRO-S V1 or V2)?
Which activities are needed to prepare HIQuad X in existing plants?
Replace legacy HIQuad modules by active ones.
  Latest CPU and COM modules of HIQuad support HIPRO-S V2.
  E.g. F 6214
Make sure, that all systems are installed referring to the present standards.
  H 7034 net filter 24 VDC
  Exchange F 3349 to latest revision AS01
  E.g. system fan K 9203A every 2nd extension rack

## Slide 47
High-end safety engineering
SILworX®
Notes: The new engineering Software Platform
Specialised for safety engineering
Manager for all HIMA safety systems and Applications
Easy and efficient through concentration on safety programming
Referent Note:
What is the USP (Unique selling point) of Software?
Today the Features between different Software Products are all similar. The difference is how this Features work in detail and how easy it is to use them.
To show the “Ease of use” is difficult. Therefore we recommend different ways to present the software:
Use SILworX_Intro_E_xx.ppt PowerPoint.
Give a live demonstration (Create a Project live)
If you have only limited presentation time or when the client is not interested in details of Engineering. The next Slides will give an main overview of the SILworX functionality

## Slide 48
SILworX® High-End Safety Engineering
  One engineering tool for HIMax®-, HIMatrix®-, and HIQuad®X-Systems
  Fully integrated configuration, programming and diagnostic environment
  IEC 61131-3 programming:
    function block diagrams (FBD),
    sequential function charts (SFC),
    structured text (ST)
  Certified function blocks
  Password protection for projects and controller access
Notes: Overview of the main Benefits and functions of SILworX.
Referent Note:
Use this slide if you have only limited presentation time or when the client is not interested in details of Engineering. This Slides will give an main overview of the SILworX functionality

## Slide 49
SILworX® High-End Safety Engineering
  Offline simulation and online test
  SIL3 comparator for hardware and logic changes
  Supports reload functionality for hardware, communication and logic changes
  Multitasking for up to 32 independent programs
  C-Code function block option for using pretested C-Code within safety systems
  Hardware import/export via XML
  Compatible with Microsoft Windows 10
Notes: Overview of the main Benefits and functions of SILworX.
Referent Note:
Use this slide if you have only limited presentation time or when the client is not interested in details of Engineering. This Slides will give an main overview of the SILworX functionality

## Slide 50
SILworX Multitasking
ESD
F&G
BMS
HIPPS
etc.
Independence in the system
  Different applications/programs
  Time-/ critical and non-critical applications
  Safe and nonsafe applications
Each program can be modified without affecting others
  Individual checksums for minimal certification effort
  Add applications interference-free
Each program with individual cycle/scan time
  Target cycle time possible for each application (controller)
SILworX Multitasking

## Slide 51
Feature in SILworX v10
Preview SMART SAFETY TEST
Permanent increasing quality requirements
and high effort to test application programs
in safety PLCs initiated the idea of
SMART SAFETY TEST

## Slide 52
„In IEC 61511 Ed2 part 1, chapter 15.2.2 SIS safety Validation:
“Validation planning for the application program shall include the following:
The technical strategy for the validation including (where relevant):
– manual and automated techniques;”
„IEC 61511 Ed2 part 2 B.2 Application program development and validation philosophy“:
Semi-automatic testing through model checking in order to verify whether each AP module meets its functional and safety specifications;
Motivation – current standards
Notes: Die Möglichkeit automatische Testabläufe im sicheren Engineering Tool zu definieren bietet Vorteile im gesamten safety Lebenszyklus.
Kunden gewinnen einen Qualitäts- und Sicherheitsvorteil bei gleichzeitiger Reduzierung der Lebeszykluskosten (OPEX) für wiederkehrende Validierungsaufgaben wie Proof-Tests oder Re-Validierung bei Änderungen.

## Slide 53
Dynamic, function orientated test can be executed.
You have the following benefits by using Smart Safety:
Ability to reproduce
Time saving
Increased test quality
Execution of regression tests
Test Management
Specification
Test Execution
Generating test cases
Test Documentation
Test Results
Test Management

## Slide 54
Supports the usage of recommended methods regarding tests and acceptance
Defined test cases are reusable
Defined test cases are up to date at any time
Automated tests can be executed without user interrupts
Automated revalidation in case of changes
Usable to support and document proof tests
Automated documentation of the test execution and results
Smart Safety Test is direct executable on the safety PLC
Smart Safety Test
Released with SILworX V10

## Slide 55
Smart Safety Test - Editor
Edit the testplan
Cross conference with goto function
Choose the global variables
Definition of test sequence
Drag & Drop
Choose the test elements

## Slide 56
Smart Safety Test - Test execution Off- / Online
Choosing for the Multitasking
Execute the test plan in offline simulation or online

## Slide 57
Test operation
Execute the test plan in offline simulation or online
Testergebnis
Comparing of test result
Test Procedure
Setting breakpoint
Smart Safety Test - Test execution Off- / Online
Notes: Test operation: start, stop, reset, export test report
Comparing of test result: set value and real value, the result will be shown in the status
Set breakpoint for each step

## Slide 58
Smart Safety Test - Test Report as PDF / csv / …

## Slide 59
Email: s.daenner@hima.com
Website: www.hima.com
HIMA Paul Hildebrandt GmbH
Albert-Bassermann-Str. 28
68782 Brühl, Germany
Phone: +49 (0) 6202 / 709-819
Fax: +49 (0) 6202 / 709-107
Thank you for your attention! Sebastian Dänner Product Manager HIQuad X Head of Component Obsolescence Management