## SFC_CSG01
| HW | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status
Sequence description |  | Fault reset |  | Start | Start conditions main burner |  |  |  |  | Tightness test main burner | [9 empty] | Pre-purging of combustion chamber | [7 empty] | Start conditions igniter |  |  |  | Automatic start igniter | [9 empty] | Start main burner |  |  |  |  | Auto. stop igniter |  | Burning | Manual start igniter parallel with main burner | [15 empty] | Manual stop igniter |  | Burning | Manual stop main burner
Initial Step No., Purging |  | >128 | >128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 17 | 17 | 17 | 17
Initial Step No., Igniter |  | >128 | >128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 15 | 15 | 15 | 15 | 16 | 17 | 18 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 16 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Initial Step No., Main burner |  | >128 | >128 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 17 | 18 | 19 | 23 | 24 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Interlock | I1 / X:14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Permissive | I2 / X:15 | — | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Purging / no purging | I3 / X:16 | 0 | 0 | 0 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 0 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Combustion air pressure > Min | I4 / X:17 | 1 | 1 | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Purging conditions | I5 / X:20 | 0 | 0 | 0 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | 1 | 1 | 1 | 0 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Igniter flame | I6 / X:21 | 0 | 0 | 0 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 0 | — | 0 | 0 | 0! | 0 | 0 | 0 | 0! | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | — | — | 0 | — | 0 | 0 | 0! | 0 | 0 | 0 | 0! | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | — | — | — | — | — | — | — | —
Igniter SSV1 close | I7 / X:22 | 1 | 1 | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | — | — | — | — | — | — | 1 | — | 1 | — | — | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | — | — | — | 1 | — | — | — | — | — | — | — | —
Igniter SSV2 close | I8 / X:23 | 1 | 1 | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | — | — | — | — | — | — | 1 | — | 1 | — | — | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | — | — | — | 1 | — | — | — | — | — | — | — | —
Main burner flame | I9 / X:26 | 0 | 0 | 0 | — | — | 0 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 0 | 0! | 0 | 0 | 1! | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | — | — | — | 0
Tightness pressure > Max | I10 / X:27 | 0 | 0 | 0 | — | — | — | — | — | — | — | — | — | — | — | 1 | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | 1 | —
Tightness pressure < Min | I11 / X:28 | 1 | 1 | 1 | — | — | — | — | — | 1 | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Main burner ignition power | I12 / X:29 | 1 | 1 | 1 | — | — | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Main burner SSV1 close | I13 / X:32 | 1 | 1 | 1 | 1 | — | — | — | 1 | — | — | — | 0 | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | 1 | — | 1 | 1 | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | — | 1
Main burner SSV2 close | I14 / X:33 | 1 | 1 | 1 | 1 | — | — | — | 1 | — | — | — | 1 | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | 1 | — | 1 | 1 | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | — | 1
Main burner relieve valve close | I15 / X:34 | 0 | 0 | 0 | — | 0 | — | — | 1 | — | — | — | 1 | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | — | — | — | 0
Main burner fuel air ratio | I16 / X:35 | 0 | 0 | 0 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | — | — | — | — | — | —
Push button START | I17 / X:38 | 0 | 0 | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | — | 1 | — | — | — | — | — | — | — | — | — | — | 1 | — | — | — | — | — | — | 1 | — | — | — | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Push button STOP igniter (NC) | I18 / X:39 | 1 | 1 | 1 | — | — | — | — | — | — | — | — | — | — | — | — | — | 1 | — | — | — | — | — | — | — | — | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | — | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | — | — | — | — | — | — | — | — | —
Push button STOP main burner (NC) | I19 / X:40 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | — | — | — | — | — | —
Fault reset | I20 / X:41 | 0 | 1 | 0 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Attemps for ignition, igniter | Parameter 7 | P7 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >1 | >1 | >1 | >1 | >2 | >2 | >2 | >2 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >1 | >1 | >1 | >1 | >2 | >2 | >2 | >2 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3 | >0 & <3
Attemps for ignition, main burner | Parameter 14 | P14 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >1 | >1 | >1 | >1 | >1 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2 | >0 & <2
Restart release timer | Parameter 3 | P3 | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Purging timer | Parameter 4 | P4 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Ready for ignition timer | Parameter 5 | P5 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Pre-ignition timer | Parameter 6 | P6 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | —
Igniter safety timer | Parameter 8 | P8 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Igniter re-ignition delay timer | Parameter 9 | P9 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Igniter re-ignition timer | Parameter 10 | P10 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Overlapping timer | Parameter 11 | P11 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Tightness test timer | Parameter 12 | P12 | — | — | — | — | — | — | — | — | Elpsd | — | — | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | —
De-pressurizing timer | Parameter 13 | P13 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Main burner safety timer | Parameter 15 | P15 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Main burner re-ignition delay timer | Parameter 16 | P16 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Main burner re-ignition timer | Parameter 17 | P17 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Fuel air ratio shutdown delay timer | Parameter 18 | P18 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Internal delay timer |  |  | — | — | — | — | — | — | — | Elpsd | — | — | — | Elpsd | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Elpsd | — | Elpsd | — | Elpsd | —
Purging preparation timer |  | 5 Min. | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Target Step No., Purging |  | >128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 17 | 17 | 17 | 17 | 17
Target Step No., Igniter |  | >128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 (15) | 8 | 9 | 10 | 11 (15) | 12 | 13 | 14 | 15 | 15 | 15 | 15 | 15 | 16 | 17 | 18 | 18 | 2 | 3 | 4 | 5 | 6 | 7 (15) | 8 | 9 | 10 | 11 (15) | 12 | 13 | 14 | 15 | 16 | 16 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Target Step No., Main burner |  | >128 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 17 (23) | 18 | 19 | 23 | 24 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
Ready for operation | O1 / X:2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Start purging | O2 / X:3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check combustion air pressure | O3 / X:4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sparking transformator | O4 / X:5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open igniter SSV1 and SSV2 | O5 / X:8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open main burner SSV1 | O6 / X:9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Open main burner SSV2 | O7 / X:10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Close main burner relieve valve | O8 / X:11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Restart release timer | Parameter 3 | P3 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start
Purging timer | Parameter 4 | P4 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Ready for ignition timer | Parameter 5 | P5 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Pre-ignition timer | Parameter 6 | P6 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | Start | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | Start | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Igniter safety timer | Parameter 8 | P8 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | Start | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | Start | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | —
Igniter re-ignition delay timer | Parameter 9 | P9 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Igniter re-ignition timer | Parameter 10 | P10 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Overlapping timer | Parameter 11 | P11 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Tightness test timer | Parameter 12 | P12 | — | — | — | — | — | — | — | Start | — | — | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | —
De-pressurizing timer | Parameter 13 | P13 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Main burner safety timer | Parameter 15 | P15 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Main burner re-ignition delay timer | Parameter 16 | P16 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Main burner re-ignition timer | Parameter 17 | P17 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Fuel air ratio shutdown delay timer | Parameter 18 | P18 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Internal delay timer |  |  | — | — | — | — | — | — | Start 1s | — | — | — | Start 3s | — | Start 1s | — | Start 1s | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | P11 | Start 0,5s | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start 0,5s | — | Start 1s | — | Start 1s | — | —
Runtime control timer, purging |  | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start 5s | Start 5s | Start 5m | — | — | — | Start 5m | P5 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | —
Error code purging |  | — | — | 256 | 256 | 256 | 256 | 256 | 256 | — | 256 | 256 | — | 256 | 256 | — | 256 | 256 | — | 131 | 132 | 133 | — | — | — | 137 | 138 (256) | 256 | — | — | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | — | 256 | — | 256 | — | — | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | — | — | — | 256 | — | — | — | 256 | 256 | — | 256 | 256 | —
Runtime control timer, igniter |  | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start 1s | Start 1s | — | — | P6 + 1s | P8 | P9 +1s | P10 +1s | P6 + 1s | P8 | P9 +1s | P10 +1s | P6 + 1s | P8 | — | — | — | — | — | — | — | Start 10s | — | Start 1s | — | — | P6 + 1s | P8 | P9 +1s | P10 +1s | P6 + 1s | P8 | P9 +1s | P10 +1s | P6 + 1s | P8 | — | — | — | Start 10s | — | — | — | — | — | — | — | — | —
Error code igniter |  | — | — | 256 | 256 | 256 | 256 | 256 | 256 | — | 256 | 256 | — | 256 | 256 | — | 256 | 256 | — | 256 | 256 | 256 | — | — | — | 256 | (129) | 130 | — | — | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 256 | 256 | 256 | 256 | 256 | 256 | — | 145 | — | 130 | — | — | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | — | — | — | 145 | — | — | — | 256 | 256 | — | 256 | 256 | —
Runtime control timer, purging |  | — | — | Start 1s | Start 1s | Start 1s | Start 2s | Start 2s | Start 2s | — | Start 2s | Start 2s | — | Start 2s | Start 2s | — | Start 2s | P4+P5+5m | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | P15 | P16+1s | P17+1s | P15 | P15 | P18+1s | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | Start 2s | Start 2s | — | Start 2s | Start 2s | —
Error code main burner |  | — | — | 129 | 130 | 131 | 132 | 133 | 134 | — | 136 | 137 | — | 139 | 140 | — | 142 | 143 | — | 256 | 256 | 256 | — | — | — | 256 | 256 | 256 | — | — | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 144 | 145 | 146 | 147 | 151 | 152 | — | 256 | — | 256 | — | — | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | — | — | — | 256 | — | — | — | 156 | 157 | — | 159 | 160 | —